The header is left blank

Design Considerations of Resonant DC/DC Converter for Fuel Cell Inverter Application 
Aleksandrs Andreiciks (M.sc.ing., Riga Technical University), Oskars Krievs (Dr.sc.ing., Riga Technical University)
Abstract – In order to use hydrogen fuel cells in domestic applications either as main power supply or backup source, their low DC output voltage has to be matched to the level and frequency of the utility grid AC voltage. Such power converter systems usually consist of a DC-DC converter and a DC-AC inverter. The paper focuses on double-stage, grid-connected Fuel Cell conversion systems. Comparison of different structures of resonant DC-DC converters, which allows reduced switching losses, are analyzed accounting the specific behavior of Fuel Cells. The converter is elaborated for 5 kW power to match the rated power of the proton exchange membrane (PEM) fuel cell
Keywords – Fuel Cell System, LLC Resonant DC/DC Converter 
I. Introduction
The research of renewable energy resources, as well as the hydrogen energy has gained a growing interest in the recent years. The hydrogen fuel cells are fully ecological, taking into account that heat and water are the only by-products, which are excreted into the environment. The typical applications of hydrogen fuel cells include electrical transport, combined heat and power generation systems. In order to utilize the electrical energy which is produced by the fuel cells, characterized by slow dynamic response, low output voltage and large voltage variations, static power converters are researched widely throughout the world. [1]
The fuel cells used in domestic application, either as main power supply or backup source, need to be connected to the grid. Thereby, their low DC voltage has to be converted by means of a power converter into AC voltage in accordance with the grid voltage parameters. Such power converter systems usually consist of a DC-DC converter and a DC-AC converter. To reach a suitable DC voltage supply for the inverter, it is necessary to use a transformer or a boost DC/DC converter. When the required voltage amplification is large, the boost topology is not appropriate due to the lack of galvanic insulation between the input and output. In such cases DC/DC converters with high frequency transformer are preferred. In order to minimize the switching losses in high frequency DC/DC converters, different topologies of resonant converters have been investigated [2], [3] using the soft-switching power conversion techniques. 

Usually, the analysis of resonant converters considers their employment in switching power supply applications where a wide range of the ratio between input and output voltages is required. In such scope, this paper provides a comparison among the most promising resonant converter topologies. Subsequently, a detailed simulation study of the most appropriate resonant converter has been carried out to be used for 5kW proton exchange membrane (PEM) fuel cell. The proposed 5kW LLC resonant converter is designed for boosting from the low input voltage (80Vdc-100Vdc) to high output voltage (400Vdc), the predicted maximum efficiency is η>95%.

II. Resonant DC/DC converters
In many years, it has been a world-wide trend to reduce the volume of the switching power supplies by increasing the switching frequency. However, the high frequency causes low efficiency because of high switching losses. Since the resonant converter has ZVS or ZCS function for reducing the switching losses, the resonant converter has been widely used in the power industry. Resonant DC/DC converters are constituted by an inverter followed by a rectifier and an output filter. Many structures may be employed to realize a resonant DC/DC converter; the two basic structures are characterized by a different position of the capacitor of the resonant circuit that can be placed in series (Series Load Resonant, SLR), or in parallel (Parallel Load Resonant, PLR) to the load. Other structures, denoted as series parallel resonant converters, employ two capacitors (LCC) or two inductances (LLC). [2]
A. Series Load Resonant Converter
The circuit diagram of a half-bridge Series Load Resonant converter is shown in Fig. 1. The two inverter switches S1 and S2 are alternatively turned on and off, with a suitable switching frequency, ƒs. According to the value of the switching frequency, the resonant converter can operate in three different modes [2].
When ƒs is smaller than  half of the resonance frequency ƒo of the Lr Cr circuit:



[image: image32.png]


.
(1)

the inverter's conduction is of discontinuous type. In this operating condition, the inverter switches turn off at zero voltage and current and turn on with a limited current slope, so 


[image: image2.emf]V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

C

oss1

n:1:1


Fig. 1. Half-bridge Series Load Resonant Converter

the switching losses are very small. However, due to the discontinuous conduction, the current peak is greater than in continuous conduction; therefore, the conduction losses increase.

When ƒs is comprised between ƒo/2 and ƒo (ƒo/2<ƒs ≤ƒo) the conduction is of continuous type. In this frequency region the commutations of the inverter switches are similar to that produced by a square wave commutating inverter with a capacitive load; i.e. the turn off occurs at zero current (ZCS) but the turn on happens at non-zero voltage and current, with significant switching losses.[1]
Also when ƒs is greater than ƒo the conduction is of continuous type. In this operating condition the commutations of the inverter switches are similar to that produced by a square wave commutating inverter with an inductive load; i.e. the turn on occurs at zero voltage (ZVS) while the turn off is characterized by significant switching losses. Nevertheless, the turn off losses can be widely reduced by inserting a suitable capacitor in parallel to each switch. In this way, both the switching and the conduction losses are adequately small.
The characteristic factor Q is the ratio between the characteristic impedance and the load. Fig. 2 shows, for different values of characteristic factor, Q defined as:


[image: image3.wmf]o

r

R

L

f

Q

0

2

p

=

.
(2)

The DC gain characteristic g is defined as: 


[image: image4.wmf]2

/

in

o

V

V

g

=

.
(3)
A ratio k between the switching frequency and the resonance frequency is:



[image: image5.wmf]0

f

f

k

s

=

.
(4)

In the Fig. 2 the transformer ratio ns/ np has been assumed as unitary. The DC gain characteristics are significant when the resonant converter is used to supply a DC load with a controlled voltage.
[image: image1.wmf]r

r

C

L

f

p

2

1

0

=


Fig. 2. DC gain characteristics of a SLR Resonant Converter
The series-resonant converter has the main disadvantage that the output voltage cannot be regulated for the no-load case. This can be seen from the characteristic resonant curves of Fig. 2. At Q = 1, for example, the curves have very little “selectivity,” and, in fact, at no load the curve would simply be a horizontal line. This means that this converter would only be used in applications where the load regulation is not required. A mean to get some no-load regulation would be to turn the converter on and off in a time ratio control fashion at a frequency much lower than the resonant frequency of the converter.

Another disadvantage of a converter is that the output dc filter capacitor must carry high ripple current. This is a significant disadvantage for applications with low output voltage and high current. For this reason the series resonant converter is not considered suitable for low output voltage high output current converters but is it rather more suitable for high-output-voltage low output current converters.
B. Parallel Load Resonant Converter 
The circuit diagram of a half-bridge Parallel Load Resonant Converter is shown in Fig.4. The behavior of the conversion system is quite similar to the previous one as concern the three operation modes. On the contrary, the DC gain characteristics are very different, as shown in Fig. 3. From these curves it is seen that, in contrast to the series-resonant converter, the converter is able to control the output voltage at no load by running at a frequency above resonance. Note also that the output voltage at resonance is a function of load and can rise to very high values at no load if the operating frequency is not raised by the regulator [1].
The main disadvantage of the parallel-resonant converter is that the current carried by the power MOSFETs and resonant components is relatively independent of load. This converter is less appropriate for applications which have a large input voltage range and which require it to operate considerably below its maximum design power while maintaining very high efficiency. Conversely, the converter is better suited to applications which run from a relatively narrow input voltage range and which present a more or less constant load to the converter near the maximum design power. Of course, the power converter must be designed thermally for the maximum power and, therefore, has no problem running at reduced power thermally only the part load efficiency is less than the full load efficiency. The parallel-resonant converter is suitable for low output-voltage high output current applications. This is due to the fact that the dc filter on the low-voltage output side of the transformer is of the inductor input type and, therefore, dc output capacitors capable of carrying very high ripple currents are not needed. The inductor limits the ripple current carried by the output capacitor. Note also that the transformer leakage inductance could be used as the resonant inductance by placing the resonant capacitor across the total span of the secondary winding. This is normally not ideal for low output voltages because the capacitor would have to carry too much ac current. However, for higher output voltage converters this 

[image: image6.emf]V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

D

1

C

oss1

n:1:1

S

2

D

2

C

oss2

L

o

C

C


Fig. 3. Half-bridge Parallel Load Resonant Converter 

[image: image7.emf]
Fig. 4. DC gain charactericteristics of a PLR Resonant converter. 

placement of the resonant capacitor may be desirable. Also, the resonant capacitor can be placed on a tertiary transformer winding [6]. 

C. LLC Resonant Converter 
The circuit diagram of a half-bridge LLC Resonant Converter is shown in Fig. 5. The behavior of the LLC conversion system is quite similar to that of the SLR as concern the three operation modes, but this circuit presents two different resonance frequencies. When diode D3 or D4 are turned on, resonant circuit becomes composed by Lr and Cr , so resonance frequency is equal to f0:


[image: image8.wmf]r

r

C

L

f

p

2

1

0

=

.
(5)
On the contrary, when both diodes are open, inductance Lm is in series to Lr ; therefore the resonance frequency becomes equal to f1 :



[image: image9.wmf]r

m

r

C

L

L

f

)

(

2

1

1

+

=

p

.
(6)

Fig. 6 shows the DC gain characteristic g of the LLC resonant converter assuming a value of Lm equal to that of Lr .

Comparing with SRC, the converter can achieve both Buck mode and Boost mode. When the switching frequency is higher than resonant frequency, voltage gain of LLC converter is always less than one, and it operates as an SRC converter and zero voltage switching (ZVS) can be achieved. When the switching frequency is lower than resonant frequency, for different load conditions, both ZVS and zero current switching (ZCS) could be achieved. At the boundary of ZVS and ZCS regions, converter voltage gain reaches it maximum value.


[image: image10.emf]V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

C

oss1

n:1:1


Fig. 5. LLC Resonant Converter.

[image: image11.emf]
Fig. 6. DC gain charactericteristics of a LLC Resonant converter. 

LLC converter displays many advantages over other resonant converter topologies; it can regulate the output over wide line and load variations with a relatively small variation of switching frequency, it can achieve zero voltage switching (ZVS) over the entire operating range, and all essential parasitic elements, including junction capacitances of all semi-conductor devices and the leakage inductance of the transformer, are utilized to achieve soft-switching [2].
III. Operational principles of llc resonant dc/dc converter

As shown in Fig. 5, the primary switches S1 and S2 conduct alternately to generate a symmetrical square waveform with the magnitude of Vin/2. D1 (D2) and COSS1 (COSS2) are the anti-paralleled diode and the equivalent output capacitor of S1 (S2). The resonant tank is formed by the resonant capacitor Cr, and the leakage inductor Lr and magnetizing inductor Lm of transformer. The center-tapped rectifier is constructed by connecting diodes D3 and D4 to the secondary windings of transformer.

The main theoretical waveforms of the LLC resonant DC/DC converter are shown in Fig. 7. There are ten operation modes within one switching period. Because the waveforms are symmetrical, only the operation principles of the first five modes are introduced referring to the equivalent circuits shown in Fig. 8. The operation principles of modes 6 to 10 are similar [3].
A. Mode 1
This mode starts when the switch S1 is turned on under ZVS. As shown in Fig. 8(a), the resonant current iLr is sine-wave and increases from negative to discharge Cr, and energy returns to the input power source. The voltage of Lm is clamped to nVO so that the magnetizing current iLm increases 
[image: image12.emf]
Fig. 7. Main waveforms of the LLC resonant converter operating with frequency ratio between f0 and f1. 

linearly from negative. The energy stored in Lm will be released through D3 to output load. When iLr reaches zero, this mode ends.
B. Mode 1
This mode starts when the switch S1 is turned on under ZVS. As shown in Fig. 8(a), the resonant current iLr is sine-wave and increases from negative to discharge Cr, and energy returns to the input power source. The voltage of Lm is clamped to nVO so that the magnetizing current iLm increases linearly from negative. The energy stored in Lm will be released through D3 to output load. When iLr reaches zero, this mode ends.
C. Mode 2
As shown in Fig. 8(b), since iLr increases from zero to positive, the input power source charges Cr and Lr, and supplies energy to output load simultaneously. The energy in Lm is released to output load continuously. When iLm reaches zero, this mode ends.
D. Mode 3
At this mode, because the voltage of Lm is still clamped to nVO, iLm remains linearly increasing. The input power source charges Lm and supplies energy to output load. The equivalent circuit is shown in Fig. 8(c).
E. Mode 4
This mode starts when iLr and iLm equal each other. Current circulating through the secondary diode D3 naturally decreases to zero, and this diode turns off under ZCS condition. The voltage spike caused by diode reverse recovery would not exist. The voltage of Lm is no longer clamped to nVO, hence, Lm is in series with Lr and participates in the resonance with Cr in the resonant tank. Because the equivalent inductance of (Lr + Lm) is much higher than Lr, as shown in Fig. 7, iLr and iLm are almost constant in this short time interval.

F. Mode 5
While S1 is turning off, the resonant current iLr is charging COSS1 and discharging COSS2 simultaneously. At the moment of vds2 decreasing to zero, the resonant current iLr flows through anti-paralleled diode D2 which provide ZVS operation for S2 turn-on. At the same time, the secondary rectifier diode D4 turns on. The voltage of Lm is clamped to nVO with reverse polarity so that the current iLm decreases linearly. The magnetizing inductor Lm is separated from the resonance with Cr. When S2 turns on under ZVS, this mode ends and enters the half cycle with symmetrical operation principles.

[image: image13.emf]V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

D

3

i

L

m

i

L

r

i

C

oss1

n:1:1

V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

D

3

i

L

m

i

L

r

i

C

oss1

n:1:1

(a) Mode 1

V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

D

3

i

L

m

i

L

r

i

C

oss1

n:1:1

(b) Mode 2

`

V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

D

3

i

L

m

i

L

r

i

C

oss1

n:1:1

(d) Mode 4

(c) Mode 3

V

FC

n

S

n

S

n

p

+

-

C

o

R

o

C

r

L

r

D

3

D

4

S

1

S

2

D

1

D

2

C

oss2

L

m

D

3

i

L

m

i

L

r

i

C

oss1

n:1:1

(e) Mode 5


Fig. 8. Equivalent circuits of different modes for LLC converter operating with frequency ratio between f0 and f1. 

IV. Design specifications and considerations
Based on the previous analysis, the practical design procedure is presented in this section. It discusses optimizing the resonant network for given input/output specifications. The LLC resonant converter design goal is to achieve minimum loss with the capability of achieve required maximum gain to ensure wide operation range. The resonant components including Lr, Cr, and Lm are the major task in design considerations.
When the switching frequency is lower than resonant frequency, there exists a flat im(t) in dead zone for ZVS while the load viewed at primary side is infinite impedance. For ease of analysis, the currents iL(t), im(t) and ip(t) are modeled as shown in Fig. 9. The resonant inductor current iL(t) is described as a linear combination of im(t) and ip(t), where ip(t) is a sine waveform and im(t) a cosine wareform in stead of triangular one. Interestingly, im(t) and ip(t) are orthogonal each other [4].
From Fig. 8(a) we have



[image: image14.wmf])

(

)

(

)

(

t

i

t

i

t

i

p

m

L

+

=

,
(7)
where



[image: image15.wmf])

sin(

2

)

(

t

n

I

t

i

s

o

p

w

p

=

,
(8)

and



[image: image16.wmf])

cos(

4

)

(

t

T

L

nV

t

i

s

s

m

o

m

w

×

=

,
(9)

where n=Np/Ns is the turns ration. In Fig. 8(a) the power drawn from supply Vdc occurs when S1 conducts during 0<t<Ts/2, i.e.


[image: image17.wmf]n

I

V

dt

t

T

L

nV

t

n

I

T

V

i

V

P

o

dc

T

S

S

m

o

S

o

S

DC

av

L

DC

in

S

2

)

cos(

4

)

sin(

2

2

/

0

,

=

ú

û

ù

ê

ë

é

÷

÷

ø

ö

ç

ç

è

æ

-

÷

ø

ö

ç

è

æ

=

=

ò

w

w

p

.
(10)

[image: image18.png]



Fig. 9. Equivalent current waveform model for iL(t), im(t) and ip(t) in LLC resonant converter.

Since Pin=Po/η, where η is the efficiency, we have:


[image: image19.wmf]n

I

V

R

I

P

o

dc

L

o

o

2

2

=

=

h

h

,
(11)

and the turns ratio n is then given by:


[image: image20.wmf]o

DC

L

o

DC

V

V

R

I

V

n

2

2

h

h

=

=

.
(12)

The ZVS behavior during the dead time Fig. 8(e), in which ip(t)=0, iL(t)=im(t)≈constant and Coos1=Coos2=Co. The required time tZVS for ZVS is then given by:



[image: image21.wmf]S

o

DC

m

o

ZVS

T

nV

V

L

C

t

8

=

.
(13)

and the maximum magnetizing inductance Lm can then be estimated by, from (12), (13).



[image: image22.wmf]o

d

S

DC

o

d

S

o

m

C

t

T

V

C

t

T

nV

L

16

8

min

,

min

,

h

=

=

.
(14)

From (10), the charge QCr in the resonant capacitor Cr at resonance can be given by:



[image: image23.wmf]n

T

I

V

Q

C

Q

S

o

DC

r

r

Cr

2

=

=

,
(15)

and we have



[image: image24.wmf]DC

r

S

o

r

V

nQ

T

I

C

2

=


(16)

and



[image: image25.wmf]2

2

)

(

r

L

r

r

Q

R

n

C

L

=

.
(17)

Due to practical considerations for the converter components, the initial switching frequency fs is presumed to be below fr for working in boost condition, we set fr = 100kHz. From (12), the turns ration is given by n=Np/Ns= 0.11875/1. A power MOSFET IRF 3077Pbf is employed as switch, with Coos1=Coos2=Co=830pF. The dead time between two gate drives is defined as 200ns. From (14), we can estimate the magnetizing inductance to be Lm< 1430μH. From (16), we can obtain Cr=7.46μF for Qr=0.3. The correspondent resonant inductances are Lr=339 nH
V. Simulations
To describe the operation of the LLC resonant converter for fuel cell application, simulation results were obtained using PLECS simulation software Fig. 10. shows a model of a 5 kW converter with 100 kHz switching frequency. Scopes are connected to measure resonant output voltage, driving pulses and load voltage. Waveforms are presented in the following 
[image: image26.png][ntegrator

— 1/s

:' | o
»| G
i
- . + /]\ Scopel > VY] I
A s = O |
] C: 7.46€-6 | L: 3.39e-7 D3 &Opez l
I N N
ml A 1 a 54\
+
. . +
V_dc L: .3e-6 C: 5e-6 = R 32
o R: 20
— +
e §E
|_
Ami D4
Tr2
Pulse -
Relational Generator
NOR Operator | || | VCO 5 Jref
Blanking Time < “l | 1 >
’ UpperLimit: 0.9
g s LowerLimit: 0.1 Ki




Fig. 10. LLC Converter schematics in PLECS environment 
[image: image27.png]



Fig. 11. Simulated waveforms of the LLC converter at full-load and 100Vdc input, from the top – S1, S2 control voltage, current through Lr and Lm, voltage of the resonant capacitor Cr..

[image: image28.png]400+





Fig. 12. Simulated waveforms of the LLC converter at full-load and 100 Vdc input, from the top – D3, D4 current, output voltage, output current.
[image: image29.png]400,,é,,”,,”,,”,f”,,”,,”,,”;,”,,”,,”,,4,,”,,”,,”,





Fig. 13. Simulated waveforms of the LLC converter at no-load and 100Vdc input,  from the top – D3, D4 current, output voltage, output current.
order: gating signals; output of the inverter; resonant tank circuit output voltage; output of the rectifier and load voltage.
As can be seen from the simulation rights the converter operates as desired, providing 400 V output voltage at rated input and load conditions. 

VI. Conclusions
In this paper, the design considerations for LLC resonant converter for fuel cell application are explored. The analyzed converter offers many advantages over other resonant converter topologies; it can control the output over wide line and load variations with a relatively small variation of switching frequency, it can achieve zero voltage switching over the entire operating range and all essential parasitic elements, including junction capacitances of all semi-conductor devices and the leakage inductance of the transformer, are utilized to achieve soft-switching.

The voltage gain characteristics were analyzed based on the theoretical analysis and computer simulation, which has confirmed the conducted analysis. Every switching component is operated in the soft switching condition of ZVS state for primary MOSFET switches and ZCS state for secondary diodes. The achieved results will be used for future work in elaboration of laboratory prototype of the LLC resonant converter.

References

[1] L. Robert and A. Steigerwald, “A Comparison of Half-bridge resonant converter topologies,” IEEE Transactions on Power Electronics, Vol. 3, No. 2, April 1988.
[2] J. F. Lazar and R. Martinelli, “Steady-State Analysis of the LLC Series Resonant Converter,” in IEEE APEC’01, 2001, vol. 2, pp. 728-735.

[3] Guan-Chyn Hsieh, “Design Considerations for LLC Series-Resonant converter in two-resonant regions” in PESC, 2007,  pp. 731-736.

[4] G. Hsieh, “Design Considerations for LLC Series-Resonant converter in two-resonant regions” in PESC, 2007,  pp. 731-736.

[5] B. Lu, W. Liu, Y Liang, Fred C. Lee, D. Jacobus and Van Wyk, “Optimal design methology for LLC Resonant Converter,” APEC 2006, pp.533-538
[6] A. Bellini, S. Bifaretti and V. Iacovone, “Resonant DC-DC converters for photovoltaic energy generation systems” SPEEDAM 2008, pp.815-820
[image: image30.png]DC gain

Frequency ratio &



A. Andreiciks was born in Riga, Latvia, in 1985. He received the B.sc.ing. and M.sc.ing degree  at Riga Technical University, Riga, Latvia in 2006 and 2008, respectively. Currently he is working towards a PH.D. degree in Riga Technical University, Riga, Latvia

He is currently an scientific assistant in the Institute of Industrial Electronics and Electrical Engineering, Riga Technical University. His main field of interest is the design and optimization of power electronic circuits for renewable energy systems.

[image: image31.jpg]


O. Krievs has received Bachelor’s (2001), Master’s (2003) and Doctor’s (2007) degrees in the field of electrical engineering at the Faculty of Power and Electrical Engineering of Riga Technical University. O. Krievs has been working in Riga Technical University since 2001 and currently is in the positions of assistant professor and leading researcher at the Department of Power and Electrical Engineering of Riga Technical University. His main research fields include active power filters, frequency converters and DC/DC converters.









PAGE  

_1364391910.unknown

_1364415993.unknown

_1364647988.vsd

_1364648374.vsd

_1364674109.vsd

_1364646023.vsd

_1364392604.unknown

_1364394794.unknown

_1364396865.unknown

_1364396946.unknown

_1364392930.unknown

_1364392360.unknown

_1364201398.unknown

_1364391022.unknown

_1364391820.unknown

_1364294544.unknown

_1364201332.unknown

_1364201384.unknown

_1364200984.unknown

