PAGE  
4

IMPACT of UNTRANSPOSED POWER LINES
Josifs Survilo (Senior researcher, Riga Technical University – RTU)

Abstract – Unbalanced power lines (whose conductors are not arranged in the vertices of equilateral triangle) without overhead grounding wire (OGW) besides Fortesque impedances Z0 and Z1=Z2 have mutual impedances Z01, Z10, Z02, Z20, Z12, Z21. At the end of the line, negative sequence and in less degree zero sequence of voltage appear which increase with load increasing. Flat phase arrangement 110 kV line with X/R=4, loaded by active load with resistance tenfold of phase conductor active resistance generates 2.54 % of negative sequence and 0.79 % of zero sequence. Inductive load generates less and capacitive – still more asymmetry. Stray capacitances and corona losses do not have any influence. Under asymmetric short circuits impact on relay protection depends on location of special phase: is it located laterally or in the middle of the flat arrangement. Digital relay protection can easier cope with the phase unbalance effect when the line is untransposed. Balanced voltage at the end of untransposed unbalanced power line can be obtained loading the line with unbalanced load.
   Key words – current sequence of three-phase system, flat phase arrangement, mutual impedances, self impedances, untransposed power line.
1. Introduction
In real power line, phase conductors rarely are situated identically with respect to each other. As a result, mutual phase inductances are slightly different for some pairs of phases. This causes unbalance of phase voltages at the end of loaded power line which is limited by standards [1]. In distribution networks European standards limit voltage unbalance factor to 2 %, in  the USA – to 3 %. Requirements grow stricter with the increase of nominal voltage [2]. The voltage unbalance is undesirable since it leads to negative consequences, primarily to overheating of electric motors, generation of harmonics, additional power losses, are detrimental for power electronic converters and adjustable speed drives [1], [2], [3]. Therefore techniques of voltage unbalance mitigation are practiced [1]. It is clear that asymmetry of power lines affect the operation of the relay protection [4], [5], 
The asymmetry in ultra high voltage transmission lines [6] calculated basing on symmetrical component method brings errors. Transposition especially in high voltage power lines, is expensive, while M. Gashimov et al. [7] claim that transposition cycles can not be prolonged. Transmission lines running in parallel require still more transpositions [8].
In the paper, consideration is made to analytically express parameters of untransposed power line without OGW and its effect on balanced load and on relay protection. Alternative to line transposition is considered.
2. Expressions for impedances

Expressions for quantities Q (voltages U and currents I are meant) in phase notation Qabc and in Fortesque notation Q012 and their reciprocal conversions are [9]:


[image: image1.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

c

b

a

abc

q

q

q

Q

;
[image: image2.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

2

1

0

012

q

q

q

Q

;
[image: image3.wmf]abc

AQ

Q

=

012

;  
[image: image4.wmf]012

1

Q

A

Q

abc

-

=

,






















 (1)
where A and A-1 are:


[image: image5.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

a

a

a

a

A

2

2

1

1

1

1

1

3

1

;
[image: image6.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

-

2

2

1

1

1

1

1

1

a

a

a

a

A

;
[image: image7.wmf]2

3

2

1

j

a

+

-

=

.























(2)

Phase conductors in flat arrangement have different distances between each other (Fig. 1). Their self impedances zxx=zd can be considered equal, while mutual impedances zxy have different reactances which are: between adjacent phases xs, between distant phases xf. In matrix lay out branch impedances Zabc are:





[image: image8.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

d

cb

ca

bc

d

ba

ac

ab

d

abc

z

z

z

z

z

z

z

z

z

Z


,




  

(3)


[image: image9.wmf]d

g

c

d

jx

r

r

z

+

+

=

;  
[image: image10.wmf]s

g

s

jx

r

z

+

=

;  
[image: image11.wmf]f

g

f

jx

r

z

+

=

;





 
[image: image12.wmf]sf

f

s

f

s

sf

jx

jx

jx

z

z

z

=

-

=

-

=

,




(4)
where rc is active resistance of phase conductor, rg – ground resistance, xd; xs, xf – self and mutual reactances.


In transposed lines mutual impedances (index ‘t’) are equal:






zab=zac=zba=zbc=zca=zcb=zt
,





(5)
in Fortesque notation:








[image: image13.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

2

1

0

012

0

0

0

0

0

0

Z

Z

Z

Z

t


,





(6)
where:






[image: image14.wmf]t

d

z

z

Z

2

0

+

=

;  
[image: image15.wmf]t

d

z

Z

Z

Z

-

=

=

2

1

 .  



(7)
Further on, quantities with index ‘.s’ will pertain to Fig. 1a phase arrangement, with ‘.m’ – to Fig. 1b arrangement if nothing is specified before.

Observing Fig. 1 and formula (3), we have:




[image: image16.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

d

s

f

s

d

s

f

s

d

s

abc

z

z

z

z

z

z

z

z

z

Z

.

; 
[image: image17.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

d

f

s

f

d

s

s

s

d

m

abc

z

z

z

z

z

z

z

z

z

Z

.

 . 
(8)
Inequality of mutual impedances creates mutual impedances (Z01; Z02; Z10; Z12; Z20; Z21) in Fortesque notation:







[image: image18.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

2

21

20

12

1

10

02

01

0

012

Z

Z

Z

Z

Z

Z

Z

Z

Z

Z

.






(9)
Relation between phase notation and Fortesque notation is:








[image: image19.wmf]1

012

-

=

A

AZ

Z

abc

.






   (10)

Basing on the expressions (3), (4), (7), and designations in Fig. 1, we receive expressions for Fortesque components of impedance in equation (5) for Fig. 1a:





[image: image20.wmf])

3

2

3

4

(

3

0

f

s

d

g

c

x

x

x

j

r

r

Z

+

+

+

+

=

;


[image: image21.wmf]sf

sf

x

j

x

Z

6

1

3

2

1

01

-

=

;
[image: image22.wmf]sf

sf

x

j

x

Z

6

1

3

2

1

10

-

-

=

;


[image: image23.wmf]sf

sf

x

j

x

Z

6

1

3

2

1

02

-

-

=

;
[image: image24.wmf]sf

sf

x

j

x

Z

6

1

3

2

1

20

-

=

;


[image: image25.wmf]sf

sf

x

j

x

Z

3

1

3

1

12

+

-

=

; 
[image: image26.wmf]sf

sf

x

j

x

Z

3

1

3

1

21

+

=

;




[image: image27.wmf])

3

1

3

2

(

2

1

f

s

d

c

x

x

x

j

r

Z

Z

-

-

+

=

=

 



   (11)
and for Fig. 1b:






[image: image28.wmf])

3

2

3

4

(

3

0

f

s

d

g

c

x

x

x

j

r

r

Z

+

+

+

+

=

;  


[image: image29.wmf]sf

x

j

Z

Z

Z

Z

3

1

20

02

10

01

=

=

=

=

;  
[image: image30.wmf]sf

x

j

Z

Z

3

2

21

12

-

=

=


 




[image: image31.wmf])

3

1

3

2

(

2

1

f

s

d

c

x

x

x

j

r

Z

Z

-

-

+

=

=

.  


   (12)
Self inductance Ld,  mutual inductance Lm  and reactances [9] are:

             
[image: image32.wmf]3

10

)

05

,

0

(lg

4605

,

0

-

·

+

·

=

r

D

L

z

d

, H/km;
           


[image: image33.wmf]3

10

lg

4605

,

0

-

-

·

=

ph

ph

z

m

D

D

L

, H/km;



 

                             
[image: image34.wmf]L

x

v

=

, Ω/km, 






   (13)
where r is phase conductor radius; Dz is distance between phase conductor and return wire in the ground [10], Dz≈930 m; Dph-ph, is distance between phase conductors; ω is circular frequency, 1/s.
Since Dz>>Dph-ph , power line with phase conductors in the vertices of equilateral triangle can be considered as balanced with Fortesque impedances Z0 and Z1=Z2 only.

Unbalanced line has additionally mutual impedances Z01 ....
It should be noted that in flat arrangement of phases with lateral location of the phase ‘a’ mutual impedances change their value with the number order change in their indices.

In further considerations length of the line is taken 1 km in order to facilitate using the specific quantities of the line.
3. Impact on single-phase-to-earth fault


For unbalanced lines, phase voltages can be expressed relying on (2):

     
[image: image35.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

·

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

-

2

1

0

2

2

012

1

1

1

1

1

1

U

U

U

a

a

a

a

U

A

U

U

U

U

c

b

a

abc

,
  (14)
where




    
[image: image36.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

·

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

2

1

0

2

21

20

12

1

10

02

01

0

2

1

0

012

I

I

I

Z

Z

Z

Z

Z

Z

Z

Z

Z

U

U

U

U

.

  (15)
Then for phase ‘a’ observing (14) and (15) at single-phase-to-earth short circuit we can write:

  
[image: image37.wmf]2

2

1

1

0

0

2

2

1

21

0

20

2

12

1

1

0

10

2

02

1

01

0

0

2

1

0

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

U

U

U

U

U

u

u

u

ph

a

+

+

=

=

+

+

+

+

+

+

+

+

+

=

+

+

=

=

(16)
where 




[image: image38.wmf]20

10

0

0

Z

Z

Z

Z

u

+

+

=

; 
[image: image39.wmf]21

1

01

1

Z

z

Z

Z

u

+

+

=

;


                 

[image: image40.wmf]2

12

02

2

Z

Z

Z

Z

u

+

+

=







  (17)

By single-phase-to-earth fault and by other types of faults (see further) their value depends on how the phase ‘a’ is located (see (11) and (12)).

For single-phase-to-earth fault [11], provision









[image: image41.wmf]ph

I

I

I

I

3

1

2

1

0

=

=

=








  (18)
holds, because condition 










[image: image42.wmf]0

=

=

=

fA

fC

fB

U

I

I







 (19)
is maintained.
Faulty phase current Iuph is:











[image: image43.wmf]S

=

u

ph

uph

Z

U

I

3

,







(20)
where summery impedance ZuΣ is:









[image: image44.wmf]2

1

0

u

u

u

u

Z

Z

Z

Z

+

+

=

S

.





(21)



Observing (18), we can overwrite (16):





[image: image45.wmf]ú

û

ù

ê

ë

é

-

+

-

+

=

1

1

2

1

1

0

1

3

1

3

1

1

u

u

u

u

u

ph

u

uph

Z

Z

Z

Z

Z

Z

I

Z

U


 (22)
and further, introducing compensation factor KuN,

               
[image: image46.wmf]1

1

2

0

3

2

u

u

u

u

uN

Z

Z

Z

Z

K

-

+

=

  (23)
apparent impedance with metallic short circuit is:





[image: image47.wmf])

1

(

3

)

1

(

1

uN

u

uN

ph

ph

u

ua

K

Z

K

I

U

Z

Z

+

=

+

=

=

S


;

(24)
For transposed line well known formulas are:



[image: image48.wmf]0

0

1

2

1

)

(

t

t

ph

Z

I

Z

I

I

U

+

+

=

;
[image: image49.wmf])

2

(

3

0

t

d

g

c

t

x

x

j

r

r

Z

+

+

+

=

;



[image: image50.wmf])

(

2

1

t

d

c

t

t

x

x

j

r

Z

Z

-

+

=

=

;

[image: image51.wmf]1

1

0

3

t

t

t

tN

Z

Z

Z

K

-

=


;
 (25)






[image: image52.wmf]1

0

2

t

t

t

Z

Z

Z

+

=

S

;

[image: image53.wmf]S

=

t

ph

tph

Z

U

I

3

;






[image: image54.wmf])

1

(

3

)

1

(

tN

t

tN

tph

ph

ta

K

Z

K

I

U

Z

+

=

+

=

S

.



 (26)
Now we can compare Zua.s , Zua.m, Zta and distance L using the specific (per kilometer) values Zsp of impedances. Distance to fault place is determined using calculated Zap (Zua and Zta ) and Zsp (Zusp and Zt.sp), rather using their imaginable components (reactances). However at the influence assessment we can use impedances Za and Zsp:








 


[image: image55.wmf]sp

a

Z

Z

l

=


.







(27)
Now we can compare Zua.s , Zua.m, Zta and distance L using the specific (per kilometer) values of just shown impedances. This will be done in section 5.
4.
Impact on balanced load

At the beginning, let us see what asymmetry appears with the three-phase short circuit at the end of the line. Phase currents are:




[image: image56.wmf]abc

abc

abc

U

Z

I

·

=

-

1

 ;

[image: image57.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

a

a

U

U

U

U

c

b

a

abc

2

1

 .  
 (28)
In Fortesque notation we have:









[image: image58.wmf]abs

AI

I

I

I

I

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

2

1

0

012


.





(29)
Symmetrical components I0 and I2 show what asymmetry is created by untransposed power lines at three-phase short circuit.


To connect balanced load, means to acquire summary matrix ZLabcΣ by summarizing the branch impedance of matrix Zabc with diagonal load matrix ZLabc :








[image: image59.wmf]Labc

abc

Labc

Z

Z

Z

+

=

S


.





 (30)
where ZLabc consists of  equal for all phases loads ZL.







[image: image60.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

L

L

L

Labc

z

z

z

Z

0

0

0

0

0

0

;






 (31)
Load current observing (28) is:








[image: image61.wmf]abc

Labc

Labc

U

Z

I

·

=

-

S

1

.






(32)
Asymmetry of voltage across the load can be determined as:




[image: image62.wmf]abc

L

L

U

A

U

.

012

·

=

;  
[image: image63.wmf]abc

L

Labc

Labc

I

Z

U

.

·

=


.

(33)
5.
Numerical results
Calculations were made on the program Matlab.


A 110 kV power line with flat arrangement of phases is taken for consideration. For phase conductor AC-300/39,   specific resistance rc=0.098 Ω/km; wire radius r =12 mm.
Distance to imaginable wire in the ground Dz=930 m.
Distance Dph-ph between adjacent phases Ds=4 m, between lateral phases Df=8 m .
Distance Dpf-pf of transposed lines Dt=1.26·Ds=5.04 m.

Further, voltages are in V, currents in A, impedances – in Ω.
On the basis of these data by (13) and (4) we have:
xd=0.72269; xs=0.3422; xf =0.29866; xsf =0.04354;
for transposed line xph-ph=xt=0.32766.

Impact on single-phase-to-earth fault.

By (17) observing (11) Zu0.s=0.248+j1.3636; Zu1.s=0.1357+j0.4023; Zu2.s=0.0603+j0.4023.
By (21)
ZuΣ.s=0.444+j2.1681;
By (23) KuN.s=0.7244+j0.2138
Apparent impedance by (24) is Zua.s=0.1357+j0.4023i;
By (27) distance to the fault is ls=1;

By (17) observing (12) Zu0.m=0.248+j1.4071; Zu1.m=0.098+j0.3805; Zu2.m=0.098+j0.3805.

By (21)
ZuΣ.m=0.444+j2.1681;
By (23) KuN.m=0.8752+j0.094;
Apparent impedance by (24) is Zua.m=0.098+j0.3805;
By (27) distance to the fault is lm=1;

By (25) Zt0=0.248+j1.378;    Zt1= 0.098+j0.395;
ZtΣ=0.444+j2.1681;     KtN=0.8109+j0.0746;
By (26) apparent impedance Zta= 1;
by (27) distance to the fault is lt=1.

The results show that for  single-phase metallic short circuit in untransposed power lines, the error do not appear if faulty phase (lateral or middle) and its specific parameters (Zu) are chosen by digital protection correctly.

Calculation of  three phase short circuit current.
By (4) zd=0.148+j0.7227; zs=0.05+j0.3422; zf=0.05+j0.2987.
For Fig. 1a, observing (8), (28), (4), we have:


[image: image64.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

+

-

-

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

·

=

-

i

i

i

a

a

Z

I

s

abc

s

abc

5594

.

1

8842

.

1

6809

.

0

5240

.

2

2471

.

2

7215

.

0

1

2

1

.

.

.
Symmetrical components I012.s by (29), their absolute value |I012.s| and current unbalance factors in percents (relative to first component) are:


[image: image65.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

-

-

=

i

i

i

I

s

1501

.

0

0935

.

0

3950

.

2

6007

.

0

0023

.

0

0273

.

0

.

012

;  
[image: image66.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

1769

.

0

4692

.

2

0274

.

0

.

012

s

I

; 
[image: image67.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

16

.

7

11

.

1

.
The same, calculated for Fig. 1b, is:

[image: image68.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

-

+

-

=

i

i

i

I

m

1562

.

0

0833

.

0

3950

.

2

6007

.

0

0248

.

0

0116

.

0

.

012

;
[image: image69.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

1770

.

0

4692

.

2

0274

.

0

.

012

m

I

; 
[image: image70.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

19

.

7

11

.

1

.
Symmetrical component proportion can be considered the same for special phase conductor lateral and middle arrangement which corresponds to physical sense.

Calculation of loaded power line. 









The resistance of balanced active load is assumed tenfold of Z1=Z2 active component Re (Z1)=R1. By (11) Z1=0.098+j0.395, hence load resistance rL=10·0.098=0.98;
by (31)



[image: image71.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

98

.

0

0

0

98

.

0

0

0

0

98

.

0

Labc

R


by (30)



[image: image72.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

+

+

+

+

+

+

+

+

=

+

=

S

7227

.

0

128

.

1

3422

.

0

05

.

0

2987

.

0

05

.

0

03422

05

.

0

7227

.

0

128

.

1

3422

.

0

05

.

0

2987

.

0

05

.

0

3422

.

0

05

.

0

07227

128

.

1

.

.

j

j

j

j

j

j

j

j

j

R

Z

Z

Labc

s

abc

s

Labc

.
Branch current observing (28); 
[image: image73.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

-

-

-

-

=

i

i

i

I

s

Labc

8813

.

0

1347

.

0

5723

.

0

6594

.

0

2884

.

0

7967

.

0

.

.
Symmetrical components IL012.s by (29), their absolute value |IL012.s| and current unbalance factor are:


[image: image74.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

-

-

+

=

i

i

i

I

s

L

0039

.

0

0217

.

0

2991

.

0

8176

.

0

0068

.

0

0008

.

0

.

012

; 
[image: image75.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

0221

.

0

8706

.

0

0069

.

0

012

s

L

I

; 
[image: image76.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

54

.

2

79

.

0

.
If active load is twice the previous value, the zero and second sequences are 0.95 and 4.11 %. Thus, with increasing load, energy quality deteriorates. It could be concluded even without doubling the load because with short circuit at the end of the line these figures were 1.1 and 7.16 %. 

Inductive load of the same value generates I0=0.62 %, I2=2.1 %, capacitive load gives I0=2.94 %, I2=4.95 %.
Voltages at the end of the line have the same proportions since they are equal to current vector matrix multiplied by diagonal load resistance matrix with equal phase values.
Calculation of symmetrical components for Fig. 1b gives the same result.
6. Impact on other types of Short circuit
The effect on three-phase fault protection can be seen in previous section calculating three-phase fault current. The zero sequence is roughly 1 % but not so easy it is with the second sequence which is more than 7 %. However this drawback can be eliminated by filtering or by per phase settings.

Phase-to-phase fault.

Preconditions [11]





[image: image77.wmf]0

=

A

I

; 
[image: image78.wmf]C

B

I

I

-

=

; 
[image: image79.wmf]0

=

-

C

B

U

U





(34)
hold. Since zero sequence is absent, hence








[image: image80.wmf]2

1

I

I

-

=

; 
[image: image81.wmf]2

1

U

U

E

-

=

-

.




(35)
Observing (15) and (35):





[image: image82.wmf]1

1

1

12

1

2

12

1

1

1

)

(

I

Z

I

Z

Z

I

Z

I

Z

U

u

=

-

=

+

=

;





[image: image83.wmf]2

2

2

21

2

2

2

1

21

2

)

(

I

Z

I

Z

Z

I

Z

I

Z

U

u

=

-

=

+

=

. 

 (36)
since







[image: image84.wmf]12

1

1

Z

Z

Z

u

-

=

; 
[image: image85.wmf]21

2

2

Z

Z

Z

u

-

=

  


(37)
and positive sequence of current is:










[image: image86.wmf]2

1

1

u

u

Z

Z

E

I

+

=

.






(38)
With specific values of Zu1 and Zu2 known, further procedures is the same as at transposed lines.

Phase-to-phase-to earth fault.

Preconditions [11]








[image: image87.wmf]0

=

=

=

c

B

A

U

U

I








(39)
hold. Since



[image: image88.wmf])

(

2

0

1

I

I

I

+

-

=

; 
[image: image89.wmf]2

0

1

U

U

U

=

=

; 
[image: image90.wmf]0

1

U

U

E

A

=

-

.
(40)





Observing (15) and (40) we have:



[image: image91.wmf]2

2

1

21

0

20

2

02

1

01

0

0

I

Z

I

Z

I

Z

I

Z

I

Z

I

Z

+

+

=

+

+

;

[image: image92.wmf]2

2

2

0

21

0

20

2

02

2

0

01

0

0

)

(

)

(

I

Z

I

I

Z

I

Z

I

Z

I

I

Z

I

Z

+

-

-

+

=

+

-

-

+





[image: image93.wmf]2

01

02

21

2

0

21

20

01

0

)

(

)

(

I

Z

Z

Z

Z

I

Z

Z

Z

Z

+

-

-

=

+

-

-

;







[image: image94.wmf]21

20

01

0

0

Z

Z

Z

Z

Z

u

+

-

-

=

;







[image: image95.wmf]01

02

21

2

2

Z

Z

Z

Z

Z

u

+

-

-

=

.




(41)
Based on (40), we can write:




[image: image96.wmf])

(

1

2

0

2

0

I

Z

Z

Z

I

u

u

u

-

+

=

; 
[image: image97.wmf])

(

1

2

0

0

2

I

Z

Z

Z

I

u

u

u

-

+

=

.
(42)
Observing (15) and (42), we have:






[image: image98.wmf]1

2

0

0

12

1

2

0

2

10

1

)

(

I

Z

Z

Z

Z

Z

Z

Z

Z

Z

U

u

u

u

u

u

u

+

-

+

+

-

=




(43)
and untransposed line first sequence impedance equals:

 




[image: image99.wmf]2

0

0

12

1

2

0

2

10

1

u

u

u

u

u

u

u

Z

Z

Z

Z

Z

Z

Z

Z

Z

Z

+

-

+

+

-

=

.


(44)
 
Further steps are the same as at transposed power lines.


Hence relay protection of untransposed lines will not have errors if specific impedances Zu will be written in the protection according to the type of fault and special phase ‘a’ displacement (lateral or middle).

The measures to diminish the effect of unbalance in digital relay protection is easier realizable when the line is not transposed because the settings of the detected faulty phase can be changed regardless of the distance to the fault while in transposed line they should be changed depending on what side of transposition place fault occurs.

Load is always affected positively by transposition.
7. Influence of stray capacitance
Verification is needed to determine whether to pay attention to stray capacitances (Fig. 2) examining untransposed lines.
Specific [10] capacitive coefficients between phase conductor and earth αaa, between adjacent phase conductors αab and between lateral conductors αac are:

[image: image100.wmf]r

h

aa

2

lg

10

4

.

41

6

·

=

a

,     
[image: image101.wmf]ab

ab

ab

D

H

lg

10

4

.

41

6

·

=

a

,

[image: image102.wmf]ac

ac

ac

D

H

lg

10

4

.

41

6

·

=

a

, (1/F)/km;

   











(45)
where r is conductor radius, h is wire height above ground, Dab is distance between adjacent wires, Dac is distance between lateral wires, Hab is distance between phase ‘a’ and the reflection of phase ‘b’ , Dab – the same for ‘a’ and ‘c’ [10].

It is convenient here to use capacitance (capacitive impedance) χ which is equal:











[image: image103.wmf]w

a

c

/

=

.







(46)
Then we have capacitive impedance matrix (for Fig. 1a):

  



[image: image104.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

C

d

s

f

s

d

s

f

s

d

cc

cb

ca

bc

bb

ba

ac

ab

aa

abc

c

c

c

c

c

c

c

c

c

c

c

c

c

c

c

c

c

c

.  
(47)
Internal impedance Zabc.i of the line is the impedance of connected in parallel Zabc and Χabc/2:
 







[image: image105.wmf]2

/

)

2

/

(

.

abc

abc

abc

abc

i

abc

Z

Z

Z

C

+

C

=


.




(48)

The task is to determine how Zabc.i  differs from Zabc.
For power line considered in section 5, we have additionally the following dimensions: h=6 m; Hab=12.65 m; Hac =14.42 m; Dab=Ds; Dac=Df (see section 5).
By (45) and (46) we have: χaa=χd= -j395540 Ω; χab=χs= -j65924 Ω; χac= -j33739 Ω.
Verification by (48) showed that Zabc.i begins to differ from Zabc only when Χabc is diminished a hundred times.

Corona conductance does not differ much from permittance even for 330 kV lines, since it does not have influence as well. Even if the impact would be, it can not be investigated as there is no data on self and mutual conductances.
8. Alternative for transposition
If unbalanced line with symmetrical load generates asymmetrical phase currents, then asymmetrical load at the end of unbalanced line can generate symmetrical phase currents. Summary matrix (30) with unbalanced load za, zb, zc looks:
[image: image106.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

+

+

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

S

c

d

s

f

s

b

d

s

f

s

a

d

Lc

s

f

s

Lb

s

f

s

La

Labc

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

z

Z























(49)
where za, zb, zc are loads of phases a, b, c at line end.
According to Inv[12] inverse matrix ZLabcΣ-1 is:




[image: image107.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

S

-

S

c

b

a

Labc

Labc

Z

Z

a

d

g

d

a

b

g

b

a

)

det(

1

1


,

(50)
where

[image: image108.wmf]2

s

Lc

Lb

a

z

z

z

-

=

a

; 

[image: image109.wmf]s

Lc

f

s

z

z

z

z

-

=

b

; 

[image: image110.wmf]f

Lb

s

z

z

z

-

=

2

g

; 
[image: image111.wmf]2

f

Lc

La

b

z

z

z

-

=

a

;
[image: image112.wmf]s

La

f

s

z

z

z

z

-

=

d

;
[image: image113.wmf]2

s

Lb

La

c

z

z

z

-

=

a

.
(51)
Load current multiplied by det(ZLabcΣ), observing (28), is:



[image: image114.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

+

+

+

+

+

=

=

S

c

b

a

Labc

abc

L

Labc

a

a

a

a

a

a

Z

I

I

a

d

g

d

a

b

g

b

a

2

2

2

)

det(

'

.  
(52)

Voltage at power line end Uend’ multiplied by det(ZLabcΣ)  is:

 
[image: image115.wmf]ú

ú

ú

û

ù

ê

ê

ê

ë

é

+

+

+

+

+

+

=

ú

ú

ú

û

ù

ê

ê

ê

ë

é

=

c

c

b

b

a

a

Labc

c

b

a

end

Z

a

a

Z

a

a

Z

a

a

I

Z

Z

Z

U

)

(

)

(

)

(

'

0

0

0

0

0

0

'

2

2

2

a

d

g

d

a

b

g

b

a

.
(53)
Voltage at the end of untransposed power line will be balanced when between phase voltages is such coherence:






[image: image116.wmf]c

end

b

end

a

end

U

a

aU

U

.

2

.

.

=

=

, 




(54)

i.e.


[image: image117.wmf]c

c

b

b

a

a

Z

a

a

Z

a

a

Z

a

a

)

(

)

(

)

(

2

2

2

a

d

g

d

a

b

g

b

a

+

+

=

+

+

=

+

+























(55)
To obtain target, two conditions can be set up observing (53):
 



 
[image: image118.wmf]b

end

a

end

aU

U

.

.

=

;  
[image: image119.wmf]c

end

a

end

U

a

U

.

2

.

=

. 


 (56)
Since only two conditions exist, in one phase load must be chosen, wherein it’s considerable that the loads in other two phases be mostly convenient for implementation in compliance with the requirement of all three phases summary load.
9. Conclusions
1. Unbalanced power lines without OGW have three  basic Fortesque impedances Z0; and Z1=Z2 and six more mutual impedances  Z01, Z10, Z02, Z20, Z12, Z21 whose value depends on phase ‘a’ lateral or middle location in flat arrangement of phase conductors. It is the result of different branch mutual reactances.
2. Magnitude of negative and zero sequence at the end of untransposed power line increases with load increasing. 110 kV line with X/R=4, loaded by active load with resistance tenfold of phase conductor active resistance generates 0.79 % of zero sequence and 2.54 % of negative sequence; same value inductive load gives 0.62 and 2.1 % respectively; capacitive load – 2.94 and 4.95 %.
3.  Stray capacity and corona losses are too small to influence asymmetry.
4. Under asymmetric short circuits, impact on relay protection depends on location of special phase: whether it is located laterally or in the middle of flat arrangement of phase conductors.
5. Digital relay protection can easier cope with the line phase unbalance effect when it is untransposed.
6. Balanced voltage at the end of untransposed power line can be obtained connecting unbalanced load.
10. References

[1] 
A. von Jouanne and B. Banerjee. „Assessment of Voltage Unbalance”, in  IEEE transactions on power delivery, vol. 16, No 4, October 2001.

[2] 
P. Paranavithana, S. Perera, D. Sutanto. „Impact of Untransposed 66 kV Sub-transmission lines on Voltage Unbalance”.Internet: www.elec.uow.edu.au/apqrc/content/papers/AUPEC/uupeco6_2.pdf. August, 2007.
[3] 
P. Giridhar Kini, R.C. Bansal, R.S. Aithal. “Impact of  voltage unbalance on the performance of  three-phase induction  motor”. Internet: www.publish.csiro.au/?act=view_file_id=SPO6007.pdf. December 14, 2009.

[4] 
J. Schlabbach, K-H. Rofalski. Power System Engineering. Weinheim: WILEY-VCH Verlag GnbH & Co. KGaA, 2008, pp.223-233.
[5] 
B. Li, F. Guo, X. Li, Z. Bo. “Circulating Unbalanced Current of EHV/UHV Untransposed Double-Circuit Lines and Their Influence on Pilot Protection”. Internet: www. deepdyve.com/lp/institute-of-electrical-and..., March 20, 2014.

[6] 
A. Wang, Q. Chen, Z. Zhou. „Effects of untransposed UHV transmission    line on fault analysis of power systems,” in transactions of Tianjin University, June 2008, Volume 14, Issue 3, pp.231-234.

[7] 
A.M. Gashimov, A.R. Kabayeva, A. Nayir. “Transmission line transposition.” Internet: www.emo.org.tr/ekler/97a39505016683c_ek.pdf.
[8] 
Fernando Calero. “Mutual Impedance in Parallel Lines – Protective relaying and Fault Location Considerations”. Internet: www.selinc.com/WorkArea/DownloadAsset.aspx?id=3488.

[9] 
Y. Hase. Handbook of Power System Engineering. Chichester, West Sussex, England: John Wiley & Sons Ltd, 2008, pp.1-44.

[10] A.Vanags. Elektriskie tīkli un sitēmas. Rīga: RTU, 2005, pp. 120-127, 133-138, (in Latvian).

[11] .
A. Ulyanov. Elektromagnitniye perehodniye processy v elektricheskich sistemach. Moskva: Energiya, 1970, pp. 316-322 (in Russian).

[12] Invertible matrix - Wikipedia, the free encyclopedia. en.wikipedia.org/wiki/invertible_matrix.
J. Survilo. Born in Kraslava, Latvia in 1936 March 26. PhD, defended in 1980 at the Urals Polytechnic Institute in the field “Power systems and the control of them “. Dr. sc. ing. earned in Riga Technical University, Latvia in 2001. After graduating from Riga Polytechnic Institute in 1960,  40 years worked as an engineer at the Riga works “Energoautomatika”. Since 2000 working in Riga Technical University as a researcher.


Previous publications: Survilo J. Impact of distributed generation on current and impedance protections. RTU 54th International Scientific Conference (D:) Proceedings, Latvia: 14 – 16 October, 2013. Survilo J. Account of losses in electricity sales. RTU 54th International Scientific Conference (D:) Proceedings, Latvia: 14 – 16 October, 2013. Survilo J. Reciprocal load-generator power losses in a grid. Latvian Journal of Physics and Technical Sciences, No 6, lpp. 48 – 53; 2013.

Address: Kronvalda 1, LV-1010, Riga.
Phone:+371 67089939,








E-mail: jahzeps@eef.rtu.lv

Fig. 1. Flat arrangement of phase conductors


a – phase ‘a’ by side; b – phase ‘a‘ in the middle





a





c





b





a





zab=zba=zs





zcc





zbb





zaa





zbc=zcb=zs





zac=zca=zf





b





a





c





zca=zac=zs





zbb





zaa





zcc





zab=zba=zs





zcb=zbc=zf





b





zaa=zbb=zcc=zd


zsf = zs – zf





Χabc/2





Χabc/2





Zabc





Fig. 2. Stray capacitances of the power line displayed as lump quantities








PAGE  

_1449588661.unknown

_1449745323.unknown

_1460724219.unknown

_1462596129.unknown

_1462853782.unknown

_1462854959.unknown

_1462855494.unknown

_1462854055.unknown

_1462854664.unknown

_1462853998.unknown

_1462596288.unknown

_1462596340.unknown

_1462596226.unknown

_1460955041.unknown

_1462595575.unknown

_1462595923.unknown

_1462596039.unknown

_1462595464.unknown

_1460811313.unknown

_1460812233.unknown

_1460813775.unknown

_1460812210.unknown

_1460724252.unknown

_1460810896.unknown

_1450235320.unknown

_1460723931.unknown

_1460724127.unknown

_1460724192.unknown

_1460723968.unknown

_1460721888.unknown

_1460723737.unknown

_1450238037.unknown

_1460702225.unknown

_1450237097.unknown

_1450184841.unknown

_1450234327.unknown

_1450234376.unknown

_1450233086.unknown

_1449806409.unknown

_1449893244.unknown

_1450098484.unknown

_1450102846.unknown

_1449895466.unknown

_1449808139.unknown

_1449806028.unknown

_1449739704.unknown

_1449742759.unknown

_1449744353.unknown

_1449744718.unknown

_1449742949.unknown

_1449740127.unknown

_1449740579.unknown

_1449739889.unknown

_1449734473.unknown

_1449738855.unknown

_1449739444.unknown

_1449738042.unknown

_1449738373.unknown

_1449737233.unknown

_1449592474.unknown

_1449733942.unknown

_1449733994.unknown

_1449634391.unknown

_1449591229.unknown

_1449538681.unknown

_1449566885.unknown

_1449569644.unknown

_1449584254.unknown

_1449584526.unknown

_1449585113.unknown

_1449587978.unknown

_1449584549.unknown

_1449584274.unknown

_1449584366.unknown

_1449582625.unknown

_1449583921.unknown

_1449581970.unknown

_1449582582.unknown

_1449580026.unknown

_1449569361.unknown

_1449569482.unknown

_1449567999.unknown

_1449569285.unknown

_1449567232.unknown

_1449538690.unknown

_1449538694.unknown

_1449538705.unknown

_1449538706.unknown

_1449538699.unknown

_1449538703.unknown

_1449538696.unknown

_1449538692.unknown

_1449538693.unknown

_1449538691.unknown

_1449538686.unknown

_1449538688.unknown

_1449538689.unknown

_1449538687.unknown

_1449538684.unknown

_1449538685.unknown

_1449538682.unknown

_1449538683.unknown

_1449538659.unknown

_1449538665.unknown

_1449538679.unknown

_1449538680.unknown

_1449538678.unknown

_1449538662.unknown

_1449538663.unknown

_1449538661.unknown

_1449538654.unknown

_1449538656.unknown

_1449538657.unknown

_1449538658.unknown

_1449538655.unknown

_1449538647.unknown

_1449538653.unknown

_1449538648.unknown

_1449538646.unknown

