Analysis of trigeneration heat, eletric and cooling loads 
Triģenerācijas siltuma, elektriskās un aukstuma slodžu analīze
D. Jaunzems, I. Veidenbergs 

Keywords: cooling load, heat load, load analysis, load projection, power load, trigeneration, tri-generation
Abstract 

Trigeneration is a simultaneous production of heat, power and cooling, where a fraction of the shaft work or residual (waste) heat is used for driven a refrigeration systems (technologies) – absorption, adsorption or ejectors cycles. It is like an extended cogeneration, but is becoming economically viable thanks to the commercial spread of absorption cooling systems. In fact, a well-projected trigeneration plant can achieve better results than cogenerative one. The results of investigations show that trigeneraton have advantages over single electricity generations and cogenerations: the total energy efficiency is higher, the emissions of CO2 and the other waste gases are lower and it has more useful energy outputs. This kind of energy production has both of the economic and environmental merits. One of the way how to research and investigating trigeneration is (users) load analyses using linear programming, mathematical models or modeling load fluctuation and its influences. 
Area of focus
The main advantage of trigeneration is that: almost usually cooling demand in residential areas is increasing than heat consumption is decreasing, e.g. typical it is in summers. The cooling load can equalize overall consumer’s heat load in summer period. Cogeneration plant is operating according to heat load and than in proportion generates electricity, and in case is high heat load (generally in winter), output of electricity overachieve demand and electricity can be supply to the grid and sell to operator. It’s environmentally friendly and economical gainfully if cogeneration plant operation is based on heat load. 

Simplified trigeneration consists of three subsystems: power plant, heat station and cooling station. The performance of whole system is depending on how the subsystems are coupled each to other. The fig. 1 represents trigeneration energy balance. 


[image: image1.emf]Fuel

100%

Trigeneration

Heat loses

Electricity

Cooling

Net losses

Heat

55%


Figure 1. Trigeneration energy balance

The economic viability of a trigeneration (similar in cogeneration) system depends primarily on matching the thermal and electrical loads of a particular site with the heat and power outputs of the system, so that the trigeneration plant runs for a maximum number of hours per year. The availability of net metering and the possibility of exporting excess electricity are also important. In many applications however, it is not possible to utilize all the available heat at certain periods of the year as the demand for space heating is greatly reduced [1].
Heat, cooling and power load profiles are independent of each other [2]. Energy demand depends on a great number of factors: the type of users and customers, sites and climatic conditions, plants supplying energetic outputs and management criteria. The final energy consumption can be summarized as follows: space heating, space conditioning and ventilating in summer, cooling, hot water, lighting or various electrical equipment. Two management philosophies are compared:

· The thermal demand management, that is the most widespread management criterion and is based on working the engine strictly following thermal demand;

· The primary energy saving management, to achieve maximum energy savings during the plant life cycle.
[image: image2.emf]
Figure 2. Average cumulative curve of winter heat consumptions, parameterized to thermal demand peak [2]
Interpolated the parameterized curves and derived an average cumulative curve for heat demand represented in Fig. 1. One of the most common choice methods is based on the cumulative curve, and in particular it is finalized to choose the prime mover size YP, to maximize the hatched area XPYP. Such area represents, in fact, the heat amount annually supplied at full load; when this area is maximized, a good part of the annual heat consumption is provided by heat recoveries in the engine, while running at elevate load levels.
Then the purpose of any combined heat, power and cooling installations is to maximize yearly amount of “cogenerated” energy and this leads to choose an engine size as large as possible, until its rated heat output is required by final users for a large number of hours [2]. For that reason is useful make analysis and projection of expected loads and loads profiles.
A procedure for optimizing energy-management of a user is described, which, starting from hourly load diagrams, derived from the optimal design, allows the determination of the design and the running conditions of a trigeneration plant. Based on the hourly electrical, thermal and cooling load diagrams it is possible to developing the model to delineate the optimal operational strategy of a trigeneration plant which maximizes short-term economic returns over a calendar year and calculates the savings over a conventional plant configuration [3]. Load profiles of the different energy products are usually independent one each other, so increasing the evaluation complexity [4]. There are a lot of mathematical programming techniques and linear programming models to determine operation strategy as a function of user demand.
The hourly energy load diagrams were therefore determined by taking into account the annual consumption, the energy absorption of each hospital service unit (technological services, heating, cooling and lighting services, etc.) and their hourly distribution, and assuming that the energy loads of each hospital service unit were constant year-round [3]. Cost-efficient operation of a trigeneration system can be planned using an optimization model based on hourly load forecasts. A long-term planning model decomposes into thousands of hourly models, which can be solved separately [5]. Programming model can solve the optimal sizing problem and optimal operational strategy, both daily and seasonal, of a trigeneration system to meet the necessary energy demand.
The optimal sizing of the two alternative plants, both in terms of the size of single components within each configuration, and in terms of the daily running of the plant as a function of a range of variables (e.g. load profiles, required temperature levels, operating temperature, time-variable step-rates for electricity purchase, tax deductions for methane, tax on electricity which is purchased and/or self-consumed, costs for emergency backup electricity provisions, and plant maintenance costs) [3].
The modeling of load fluctuation considers the existence of higher and lower loads in the real operation of industrial processes and how much this influences the equipment capacities, imposing off-design conditions to the generating plant. Several possibilities of load management and actions may be considered for substantial peak reduction, but they are not considered in this analysis [6]. Taking into account that thermal, power and cooling loads and demand vary in time; trigeneration plant must be designed to carry under thermal-, electric- or cooling-following strategy or method.
Based on the available data from the process thermal, electric and cooling load demand, higher and lower fluctuations can be modeled (see Fig. 2) by calculating the area above its mean value according to Eq. (1).
[image: image3.wmf]å

D

-

=

i

m

i

a

L

L

E

)

(











(1)
Where Lm is the load mean value, Li is the instantaneous load above the mean value and Δ is the time interval for measuring Li (in this case-study Δ = 15 min for electric load measurement, and Δ = 4 h for thermal load measurement). The equivalent area below the mean value, that represents no consumed energy and eventually a surplus to be commercialized, is obtained by Eq. (2) [6]. Considering that for now cooling demand and load is not modeling and calculated in this analyze.


[image: image4.wmf]å

D

-

=

j

j

m

b

L

L

E

)

(











(2)
In this case, Lj is the instantaneous load below the load mean value. The procedure is based on the electric system contractual basis, in which several instantaneous values are known but just one random value in the time interval of 15 min is recorded, and considered by analogy to the thermal case with time interval of 4 h.
The mean consumed energy for the whole period T is expressed by Eq. (3).


[image: image5.wmf]T

L

E

m

´

=












(3)
The energy consumed and not consumed, respectively, above and below the load mean value is described at Fig. 2.
[image: image6.emf]
Figure 2. Modelling of load demand [6]
Fig. 3 also illustrates the final distribution of areas for a time interval T taken as unitary for simplicity. ε is the fraction of time interval in which upper and lower load occur and (1-2 ε) is the fraction of load mean value [6].
[image: image7.emf]
Figure 3. Load demand in terms of upper and lower energy [6]
Considered thermal and electric (and cooling) load fluctuation and fluctuation modelling effects to trigeneration plant design and operation strategy can be usefull for research the configuration and for calculation (apprise) the economic results in a feasibility study of a trigeneration plant.
References

1. J. Godefroy, R. Boukhanouf, S. Riffat, Design, testing and mathematical modeling of small-scale CHP and cooling system (small CHP-ejector trigeneration), Applied Thermal Engineering 27 (2007) 68–77;
2. E. Cardona, A. Piacentino, A methodology for sizing a trigeneration plant in mediterranean areas, Applied Thermal Engineering 23 (2003) 1665–1680;
3. P. Arcuri, G. Florio, P. Fragiacomo, A mixed integer programming model for optimal design of trigeneration in a hospital complex, Department of Mechanical Engineering-University of Calabria, Arcavacata di Rende, 87030 Cosenza, Italy, 2005.

4. E. Cardona, A. Piacentino, Optimal design of CHCP plants in the civil sector by thermoeconomics, Department of Energetic and Environmental Researches, Faculty of Engineering, University of Palermo, Viale delle Scienze, 90128 Palermo, Italy, 2007.
5. Aiying Rong, Risto Lahdelma, An efficient linear programming model and optimization algorithm for trigeneration, Applied Energy 82 (2005) 40–63;
6. Mario A. Basulto Ernst, Jose A. Perrella Balestieri, Influences of thermal and electric load fluctuations in the cogeneration attractiveness, Applied Thermal Engineering 26 (2006) 1500–1505.
Jaunzems Dzintars, PhD student
Riga technical university, Institute of Energy Systems and Environment
Address: Kronvalda boulv. 1, LV-1010, Riga, Latvia
Phone: +371 26108494, Fax: +371 7089908
e-mail: dz-j@inbox.lv
Veidenbergs Ivars, Dr. habil sc. ing., Professor
Riga technical university, Institute of Energy Systems and Environment

Address: Kronvalda boulv. 1, LV-1010, Riga, Latvia

Phone: +371 7089908, Fax: +371 7089908

E-mail: ivars.veidenbergs@eef.rtu.lv
Jaunzems D., Veidenbergs I., Triģenerācijas siltuma, elektriskās un aukstuma slodžu analīze
Rakstā ir detalizēti aplūkota triģenerācijas iekārtu vispārīga uzbūve un darbības principi, kā arī to priekšroсības un iespējas. Veikta slodžu analīze, interpolējot grafikus ar parametriem, izveidots atvasināta vidēja kopējā siltuma patēriņa grafiks. Izvērtētas īstermiņa un ilgtermiņa triģenerācijas iekārtas optimizācijas procedūras un stratēģija (dienas un sezonālā), kā arī identificētas to galvenās mērķfunkcijas un pamatelementi. Optimizācijas procedūras sasaistītas ar enerģētiskās saimniecības organizāciju un uzlabošanu. Saistībā ar optimizācijas procedūrām, definēti galvenie enerģijas (enerģētiskās) bilances – elektroenerģijas, siltumenerģijas un dzesēšanas enerģijas bilanču – ierobežojumi, kuri ietver sevī arī siltuma, elektriskās un aukstuma slodzes, kā arī citi siltumtehniskie parametri. Pamatojoties uz šiem enerģijas (enerģētiskās) bilances ierobežojumiem un balstoties uz elektriskās, siltuma un aukstuma ik stundu slodžu diagrammām, sākta triģenerācijas iekārtas optimālu konstrukciju un uzbūvi aprakstoša matemātiska un programmējama modeļa izstrāde, lai attēlotu optimālo triģenerācijas darbības stratēģiju, kas palielina ekonomiskos ieguvumus un finansiālos ietaupījumus īstermiņa periodā un identificē arī citus saistītos un izmērāmus lielumus. Lai noteiktu sākuma investīciju un amortizācijas izdevumu ietekmi uz investīciju atdevi, pielietoti dažādi ekonomiskie indikatori. Veikta siltuma, elektriskās un aukstuma slodžu izmaiņu un svārstību analīze triģenerācijas režīmā.    

Jaunzems D., Veidenbergs I., Analysis of trigeneration heat, electric and cooling loads
In the paper is implemented a general evaluation of trigeneration, including an analysis of different components and operation principles. The main advantages and facilities are identified.  In loads analysis was interpolated the parameterized curves and derived an average cumulative curve for heat demand. Appraised a short-term (the solar year) and a long-term optimization procedures and strategy (both daily and seasonal), recognized their objective functions and basic elements. Optimization procedures are tieback with energy-management organizing and improvement. Responsibility to optimization procedures, define head energy balance constrains – electric balance, thermal balance and cooling balance constrains as well as other heat engineering parameters. On this bases energy balance constrains and based on the hourly electrical, thermal and cooling load diagrams was started developing of the mathematical model to delineate the optimal operational strategy and design of a trigeneration plant which maximizes short-term economic returns over a calendar year and calculates the savings over a conventional plant configuration or other specifically measurement values. To determine the effects that initial investment costs and amortizations have on investment return, economic indicators were used. Perform trigeneration thermal, electric and cooling fluctuations influences analysis.
яунзeмc Д., Beйдeнбepгc и. Aнaлиз тепловой, электрическoй нагрузкu u холодоснабжение в режимe тригeнepaцuй
В статьe пoдробно рассмотрено общая строение тригeнepaцuоной установки и структурный процесс работы, а тагже её преимущества и возможности. Проделан анaлиз нагрузки, интерполированы графики с показателями, создан средний общий график расхода теплоты производной величини.  Pасценивано краткосрочные и долгосрочные оптимизирующые процедуры и стратегия (дневной и сезонный) тригeнepaцuоной установки, равномерно идентифицированы главные целевые функций и основные элементы. Оптимизирующые процедуры увязаны с организацой и усовершенствованием энергохозяйства. В связи с оптимизирующямы процедурамы, определены главные ограничения энергетического баланса - тепловой энергий, электроэнергий и энергий холодоснабжение, равномерно с другимы теплотехническимы параметрамы. Исходя на этих ограничений энергетического баланса и основаяс на диаграммы всечасной нагрузкu тепла, электроэнергий u холодоснабжение, начата разработка математического моделья, чтобы изобразить оптимальную стратегию работы тригeнepaцuй, что увеличит экономические показатели и сбережения финансовых ресурсоф в краткосрочным периоде времени и позволит идентифицировать другие сопричастные величины. Чтобы определить влияние первоначальных инвестиций и затраты на амортизацию на эффективность инвестиции, применины разные экономические индикаторы. Проведен анализ колебания тепловой, электрическoй нагрузкu u холодоснабжение в режимe тригeнepaцuй.  
_1241499369.unknown

_1241499984.unknown

_1241500190.unknown

_1237643655.vsd
�

Fuel
100%�

Trigeneration�

Heat loses�

Electricity�

Cooling�

Net losses�

Heat
55%�


